## Discussion and Directions
Read Me |  |  | How To Use
The Probability Calculation worksheet will perform the calculations required to size |  | 1 | Open Input Values Worksheet and input:
| your HVAC system components when a lab HVAC system is equipped with both |  |  | The number of each size hood
| variable air volume and automatic sash positioning. |  |  | The average observed probability of hood usage during the workday.
The safety factor you would like to use. See discussion below.
Input values are required for: |  |  |  | The acceptable probability of Limited Failure.
| The number and size of fume hoods |  |  | Design CFM per Ton of Cooling
| The average probabilityof a user standing at the hood face at any given moment during the work day. |  |  | Estimated cost of an installed ton of cooling.
The desired safety factor. This factor increases the probability of use that the calculator uses.
| The point at which limited failure could occur (Example- 99.95% - See "What the calc tells us"). | 2 | Regarding the safety factor you use.
Design CFM per Ton of Cooling. 200 CFM/ton is an average value.
| Estimated cost of an installed ton of cooling. $2000/ton is an average value. |  |  | Note that you may provide different safety factors for different
equipment depending on how critical that equipment is.
The input value for the probability that a user will be using the hood should be the observed probability
| during normal working hours. Do not adjust this value for the time when no one is working |  |  | For example, having sufficient air flow at all times is more critical than
| within the laboratory, i.e. evenings and weekends. Observations should be done |  |  | having sufficient heating and cooling.
discretely to avoid modifying the normal behavior of the lab personnel.
Since heating and cooling systems are sized for the peak loads,
When running these calculations, you may wish to change your safety factor when sizing equipment |  |  |  | the probability that the maximum number of hoods being open will coincide
| based on how critical that particular piece of equipment is. For lab ventilation, |  |  | with the hottest or coldest periods reduces the likelyhood of failure.
the most critical equipment is the air flow. The heating and cooling systems are
| less critical, and are already sized for the worst degree day, so you may consider |  |  | Finally, the impact of a few minutes of reduced heating or cooling capibility
| a smaller safety factor when doing the calculations for that equipment. |  |  | is substantially less impactful than the affect of reduced airflow.
Note that you can use the same formula to calculate flow rates for ducts that service only a portion |  | 3 | Read the Results on the Right Sizing Worksheet
| of the lab. Just modify the set up as if that section were the whole. |  |  | The results tell us, for example:
For 100 five foot hoods, a 99.95% probability, a safety factor of 2, and an observed
What the Probability Calculation worksheet tells us: |  |  |  | observed probability of use of the fume hoods of 5%, that if we design a system
| We can design a system capable of heating, cooling, supplying and exhausting the |  |  | capable of delivering 30,800 CFM, then we will have provided sufficient
| design exhaust value, and 99.95% [or whatever input value we use] of the time |  |  | capacity such that - If the average number of users are using
| we will not have a limited failure even if suddenly [the safety factor] times more hoods |  |  | their hoods doubles, then 99.95% of the time we will not have a limited failure.
are opened on the average than the proportion we have observed.

## Input Values
Values Input Here are used in Calculations
on the Right Sizing Worksheet
Number of Ten Foot Hoods | 5
Number of Eight Foot Hoods | 10
Number of Six Foot Hoods | 15
Number of Five Foot Hoods | 20
Number of Four Foot Hoods | 25
Observed Average Probability of Active Hood Use | 7%
Safety Factor | 2
1-Probability of Limited Failure | 99%
Full Open Height (Feet) | 2.33
1/2 Open Height (feet) | 1.5
Design Cooling CFM per Ton | 200
Cost of One Installed Ton of Cooling | 2000

## Right Sizing
Calculations for Facility Equipment Sizing
|  | Total Number of Hoods | 75 |  |  |  |  | Individual Hood Details
|  | Probability of Active Use | 7% |  |  |  |  | Nominal | 10 | 8 | 6 | 5 | 4
|  | Safety Factor | 2 |  |  |  |  | Hood Length
|  | Probability for Calculation | 14% |  |  |  |  | Open | 9.3333 | 7.3333 | 5.3333 | 4.3333 | 3.3333
|  | 1-Probability of Limited Failure | 99% |  |  |  |  | Hood Length
|  | Max Hoods Open | 18 |  |  |  |  | Height | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
|  | Full Open (when open) Design CFM | 35846.3333 | <<<<<<< |  |  |  | 1/2 Open
|  | Half Open (when open) Design CFM | 26633.3333 | <<<<<<< |  |  |  | Height | 2.33 | 2.33 | 2.33 | 2.33 | 2.33 | `
| For Comparison: | [6 empty] | Full Open
|  | Design CFM for Constant Volume System at Full Sash Height | 86210 |  |  |  |  | CFM | 466.6667 | 366.6667 | 266.6667 | 216.6667 | 166.6667
|  | Design CFM for Constant Volume System at 18" Sash Height | 55500 |  |  |  |  | Closed Hood
[8 empty] | CFM Half | 1400 | 1100 | 800 | 650 | 500
Open
|  | Using VAV with ASPS means you can design for | 35846.3333 | CFM Full Open |  |  |  | CFM Full | 2174.6667 | 1708.6667 | 1242.6667 | 1009.6667 | 776.6667
|  | Or you could design for | 26633.3333 | CFM Half Open |  |  |  | Open
|  | This results in a reduction of design CFM of | 50363.6667 | CFM for full open designs or
|  |  | 28866.6667 | CFM for half open designs
Impact of Total Project Cost
|  | Approx Cost of ASPS - Cooling Equipment Savings | 48833.3333 | Parenthesis = reduction in cost of project
Additional Savings associated with Heating Equipment, Air Handlers,
Exhaust Fans and Reduced Ductwork Sizes should also be considered.
[8 empty] | # of Hoods by Size | 5 | 10 | 15 | 20 | 25
| If the various sizes were the only hoods, calculate the max number open - for use in finding worst case scenario |  | Max # Open |  |  |  |  | Lineal Ft of Hood Opening by Size | 46.6667 | 73.3333 | 80 | 86.6667 | 83.3333
|  | Max 10 foot Hoods Open | 3 | [6 empty] | Total Lineal Foot of Hood Opening for the Project | 370
|  | Max 8 foot Hoods Open | 4
|  | Max 6 foot Hoods Open | 6
|  | Max 5 foot Hoods Open | 7
|  | Max 4 foot Hoods Open | 8 |  |  | Design CFM is an Open Hood is assumed to be 1/2 Open or Fully Open
The worst case is with the most large hoods open.
| For an open hood count of: | 18 |  |  |  | Full Open Design CFM |  |  |  |  | Half Open Design CFM
|  | The worst case would be if the following condition: | Open | Closed |  | Open Hoods |  | Close Hoods |  |  | Open Hoods |  | Close Hoods
|  | 10 foot Hoods | 3 | 2 |  | 6524 |  | 933.3333 |  |  | 4200 |  | 933.3333
|  | 8 foot Hoods | 4 | 6 |  | 6834.6667 |  | 2200 |  |  | 4400 |  | 2200
|  | 6 foot Hoods | 6 | 9 |  | 7456 |  | 1600 |  |  | 4800 |  | 1600
|  | 5 foot Hoods | 5 | 15 |  | 5048.3333 |  | 1083.3333 |  |  | 3250 |  | 1083.3333
|  | 4 foot Hoods | 0 | 25 |  | 0 |  | 4166.6667 |  |  | 0 |  | 4166.6667
[5 empty] | Totals | 25863 |  | 9983.3333 |  | Totals | 16650 |  | 9983.3333
[7 empty] | Grand Total | 35846.3333 |  |  |  | Grand Total | 26633.3333
Capital Cost of Construction
Calculations are for 1/2 open CV hoods vs VAV with ASPS
| Reduction in Cooling Equipment Size (Tons) |  | 144.3333
| Reduction in Cooling Equipment Cost |  | 288666.6667
| Approx Cost ASPS (in quantity) |  | 337500
| Effect on Project Cost |  | 48833.3333 | Parenthesis indicate reduction in cost of project

## Chart
SAFETY FACTORS

## Right Sizing for chart
Calculations for Facility Equipment Sizing
|  | Number of Hoods | 75
|  | Probability of Active Use | 7%
|  | Probability for Calculation | 0%
|  | 1-Probability of Limited Failure | 99%
Safety Factors for Chart
| 1 | 2 | 3 | 4 | 5
1 | 0.024429 | 0.00014931 | 4.1849e-07 | 5.8187e-10 | 3.7559e-13
2 | 0.068032 | 0.0008993 | 4.116e-06 | 8.3724e-09 | 7.483e-12
3 | 0.1246 | 0.0035624 | 2.6624e-05 | 7.9228e-08 | 9.8046e-11
4 | 0.16882 | 0.010439 | 0.00012739 | 5.546e-07 | 9.5029e-10
5 | 0.18044 | 0.02413 | 0.00048086 | 3.0626e-06 | 7.2661e-09
6 | 0.15845 | 0.045828 | 0.0014913 | 1.3895e-05 | 4.5646e-08
7 | 0.11756 | 0.073538 | 0.0039075 | 5.3265e-05 | 2.4227e-07
8 | 0.075211 | 0.10176 | 0.008829 | 0.00017607 | 1.1089e-06
9 | 0.042144 | 0.12332 | 0.017472 | 0.00050973 | 4.445e-06
10 | 0.020936 | 0.13249 | 0.030653 | 0.0013083 | 1.5797e-05
11 | 0.0093116 | 0.12745 | 0.048149 | 0.0030065 | 5.0262e-05
12 | 0.003738 | 0.11066 | 0.068262 | 0.0062356 | 0.00014434
13 | 0.0013635 | 0.087298 | 0.087936 | 0.011752 | 0.00037666
14 | 0.0004545 | 0.062936 | 0.10352 | 0.020239 | 0.00089819
15 | 0.00013912 | 0.041664 | 0.11191 | 0.032008 | 0.0019668
16 | 3.9267e-05 | 0.025435 | 0.11155 | 0.046678 | 0.0039714
17 | 1.0258e-05 | 0.01437 | 0.10291 | 0.063 | 0.0074217
18 | 2.4878e-06 | 0.0075378 | 0.088149 | 0.078945 | 0.012877
19 | 5.6177e-07 | 0.0036812 | 0.070296 | 0.092102 | 0.020801
20 | 1.1839e-07 | 0.001678 | 0.052322 | 0.10029 | 0.031362
21 | 2.3339e-08 | 0.00071541 | 0.036427 | 0.10215 | 0.044228
22 | 4.312e-09 | 0.00028586 | 0.023767 | 0.097503 | 0.058456
23 | 7.4789e-10 | 0.00010723 | 0.014559 | 0.087376 | 0.072532
24 | 1.2197e-10 | 3.7823e-05 | 0.0083851 | 0.073623 | 0.08462
25 | 1.8728e-11 | 1.2561e-05 | 0.004547 | 0.058407 | 0.092952
26 | 2.7108e-12 | 3.9322e-06 | 0.0023244 | 0.043681 | 0.096252
27 | 3.703e-13 | 1.1617e-06 | 0.0011214 | 0.030828 | 0.094059
28 | 4.778e-14 | 3.242e-07 | 0.000511 | 0.020552 | 0.086823
29 | 5.8286e-15 | 8.5535e-08 | 0.00022015 | 0.012953 | 0.075769
30 | 6.7269e-16 | 2.1351e-08 | 8.973e-05 | 0.007724 | 0.062558
31 | 7.3499e-17 | 5.0454e-09 | 3.4624e-05 | 0.0043603 | 0.048898
32 | 7.6067e-18 | 1.1293e-09 | 1.2655e-05 | 0.0023316 | 0.036203
33 | 7.4605e-19 | 2.3956e-10 | 4.3835e-06 | 0.0011815 | 0.025401
34 | 6.9367e-20 | 4.8173e-11 | 1.4394e-06 | 0.00056758 | 0.016896
35 | 6.1162e-21 | 9.1866e-12 | 4.4822e-07 | 0.00025856 | 0.010657
36 | 5.1151e-22 | 1.6617e-12 | 1.3239e-07 | 0.00011172 | 0.0063762
37 | 4.0582e-23 | 2.8512e-13 | 3.7093e-08 | 4.5797e-05 | 0.0036189
38 | 3.0546e-24 | 4.6415e-14 | 9.8603e-09 | 1.781e-05 | 0.0019487
39 | 2.1812e-25 | 7.1685e-15 | 2.4867e-09 | 6.5709e-06 | 0.00099547
40 | 1.4776e-26 | 1.0503e-15 | 5.9491e-10 | 2.2998e-06 | 0.00048242
41 | 9.4942e-28 | 1.4595e-16 | 1.35e-10 | 7.6349e-07 | 0.00022175
42 | 5.785e-29 | 1.9234e-17 | 2.905e-11 | 2.4036e-07 | 9.666e-05
43 | 3.3417e-30 | 2.403e-18 | 5.9264e-12 | 7.1735e-08 | 3.9944e-05
44 | 1.8293e-31 | 2.845e-19 | 1.1457e-12 | 2.0289e-08 | 1.5642e-05
45 | 9.4851e-33 | 3.1905e-20 | 2.0981e-13 | 5.4353e-09 | 5.8023e-06
46 | 4.6561e-34 | 3.3873e-21 | 3.6373e-14 | 1.3785e-09 | 2.0376e-06
47 | 2.1624e-35 | 3.4023e-22 | 5.9658e-15 | 3.3078e-10 | 6.7698e-07
48 | 9.4944e-37 | 3.2309e-23 | 9.2508e-16 | 7.5038e-11 | 2.1264e-07
49 | 3.9378e-38 | 2.8982e-24 | 1.355e-16 | 1.608e-11 | 6.3091e-08
50 | 1.5412e-39 | 2.4533e-25 | 1.873e-17 | 3.2517e-12 | 1.7666e-08
51 | 5.6866e-41 | 1.9577e-26 | 2.4406e-18 | 6.1987e-13 | 4.6629e-09
52 | 1.9755e-42 | 1.4709e-27 | 2.9943e-19 | 1.1126e-13 | 1.1588e-09
53 | 6.4527e-44 | 1.0391e-28 | 3.4541e-20 | 1.8776e-14 | 2.7078e-10
54 | 1.9787e-45 | 6.8918e-30 | 3.7408e-21 | 2.9749e-15 | 5.9402e-11
55 | 5.6867e-47 | 4.2837e-31 | 3.7967e-22 | 4.4172e-16 | 1.2213e-11
56 | 1.5287e-48 | 2.4905e-32 | 3.6045e-23 | 6.135e-17 | 2.3486e-12
57 | 3.8354e-50 | 1.3514e-33 | 3.1939e-24 | 7.9528e-18 | 4.2155e-13
58 | 8.9592e-52 | 6.8277e-35 | 2.6348e-25 | 9.5982e-19 | 7.0444e-14
59 | 1.943e-53 | 3.2026e-36 | 2.0181e-26 | 1.0755e-19 | 1.0929e-14
60 | 3.9e-55 | 1.3903e-37 | 1.4305e-27 | 1.1153e-20 | 1.5694e-15
61 | 7.2184e-57 | 5.5653e-39 | 9.3509e-29 | 1.0666e-21 | 2.078e-16
62 | 1.2269e-58 | 2.0458e-40 | 5.6129e-30 | 9.366e-23 | 2.5265e-17
63 | 1.9055e-60 | 6.872e-42 | 3.0788e-31 | 7.5159e-24 | 2.8073e-18
64 | 2.6892e-62 | 2.0976e-43 | 1.5345e-32 | 5.4804e-25 | 2.8343e-19
65 | 3.4255e-64 | 5.7786e-45 | 6.9031e-34 | 3.6067e-26 | 2.5827e-20
66 | 3.9065e-66 | 1.4253e-46 | 2.7803e-35 | 2.1252e-27 | 2.1071e-21
67 | 3.9498e-68 | 3.1168e-48 | 9.9278e-37 | 1.1102e-28 | 1.5241e-22
68 | 3.4976e-70 | 5.9692e-50 | 3.1047e-38 | 5.0792e-30 | 9.6548e-24
69 | 2.6708e-72 | 9.8582e-52 | 8.3727e-40 | 2.0039e-31 | 5.2741e-25
70 | 1.7231e-74 | 1.3756e-53 | 1.9077e-41 | 6.6796e-33 | 2.4342e-26
71 | 9.1333e-77 | 1.577e-55 | 3.5712e-43 | 1.8293e-34 | 9.2304e-28
72 | 3.8192e-79 | 1.4262e-57 | 5.2739e-45 | 3.9522e-36 | 2.7612e-29
73 | 1.1814e-81 | 9.5413e-60 | 5.7614e-47 | 6.3163e-38 | 6.1102e-31
74 | 2.4033e-84 | 4.1979e-62 | 4.1392e-49 | 6.6388e-40 | 8.8922e-33
75 | 2.4119e-87 | 9.1118e-65 | 1.4671e-51 | 3.4423e-42 | 6.3842e-35
76 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
77 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
78 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
79 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
80 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
81 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
82 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
83 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
84 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
86 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
87 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
88 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
89 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
90 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
91 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
92 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
93 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
94 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
96 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
97 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
98 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
99 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
100 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
101 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
102 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
103 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
104 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
105 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
106 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
107 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
108 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
109 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
110 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
111 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
112 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
113 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
114 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
115 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
116 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
117 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
118 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
119 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
120 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
121 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
122 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
123 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
124 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
125 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
126 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
127 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
128 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
129 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
130 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
131 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
132 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
133 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
134 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
135 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
136 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
137 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
138 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
139 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
140 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
141 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
142 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
143 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
144 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
145 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
146 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
147 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
148 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
149 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
150 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!