## Discussion and Directions
Read Me |  |  | How To Use
The Energy Savigs Worksheet will perform the calculations required to |  | 1 | Open Input Values Worksheet and input:
| estimate the energy savings that will be realized by the installation of the |  |  | The number of each size hood
| New Tech Automatic Sash Positioning System on your VAV Fume Hoods. |  |  | The average observed probability of hood usage during the workday.
The Full Open and Half Open Sash Heights
Input values are required for: |  |  |  | The cost of an annual CFM of Air
| The number and size of fume hoods. |  |  |  | Estimate the cost of an annual CFM of Air from the
| The average probabilityof a user standing at the |  |  |  | USDOE's LBNL Website. A link is available on our
| hood face at any given moment during the work day. |  |  |  | website.
Full Open and Half Open Sash Heights
| The cost of an annual CFM of Air | 2 | Read the Results on the Energy Savings Worksheet
The results tell us, for example:
Please make all changes on the Input Values Worksheet. |  |  |  | For 100 five foot hoods, a 99.95% probability, a safety factor of 2, and an observed
observed probability of use of the fume hoods of 5%, that if we design a system
capable of delivering 30,800 CFM, then we will have provided sufficient
capacity such that - If the average number of users are using
their hoods doubles, then 99.95% of the time we will not have a limited failure.

## Input Values
Values Input Here are used in Calculations
on the Energy Savings Worksheet
Number of Ten Foot Hoods | 5
Number of Eight Foot Hoods | 10
Number of Six Foot Hoods | 15
Number of Five Foot Hoods | 20
Number of Four Foot Hoods | 25
Observed Average Probability of Active Hood Use | 7%
Full Open Height (Feet) | 2.33
1/2 Open Height (feet) | 1.5
Cost per Annual CFM | 5

## Energy Savings
Calculations for Fume Hood Energy Use
Individual Hood Details
[5 empty] | Exhaust Volume for Constant Volume System at Full Sash Height: |  | 86210 | CFM | Nominal | 10 | 8 | 6 | 5 | 4
[5 empty] | Exhaust Volume for Constant Volume System at 18" Sash Height: |  | 55500 | CFM | Hood Length
[5 empty] | Exhaust Volume for VAV with ASPS: |  | 19191.8493 | CFM | Open | 9.3333 | 7.3333 | 5.3333 | 4.3333 | 3.3333
[5 empty] | Cost per Annual CFM |  | 5 |  | Hood Length
[9 empty] | Height | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
[7 empty] | If your hoods are at maximum exhaust volume when open to 1/2 sash height |  | 1/2 Open
[5 empty] | Average CFM Saved by Installing the ASPS and VAV |  | 36308.1507 | CFM | Height | 2.33 | 2.33 | 2.33 | 2.33 | 2.33
[5 empty] | Energy Savings from Installing VAV with ASPS | 181540.7534 |  |  | Full Open
[9 empty] | CFM | 466.6667 | 366.6667 | 266.6667 | 216.6667 | 166.6667
Closed Hood
[7 empty] | If your hoods are at maximum exhaust volume when open to Full Sash Height |  | CFM Half | 1400 | 1100 | 800 | 650 | 500
[5 empty] | Average CFM Saved by Installing the ASPS and VAV |  | 67018.1507 | CFM | Open
[5 empty] | Energy Savings from Installing VAV with ASPS | 335090.7534 |  |  | CFM Full | 2174.6667 | 1708.6667 | 1242.6667 | 1009.6667 | 776.6667
Open
| Calculations for Fume Hoods with VAV and ASPS | [8 empty] | Convert Probability of Use During Work Day
to Probability of use for all year.
|  |  | Per Hood Values |  |  |  |  | All Hoods |  | Active use during work day | 7%
|  |  | % of Year Open | CFM Open | % of Year Closed | CFM Closed | Average CFM |  |  | Total Hours per Year | 8760
| Number of Ten Foot Hoods | 5 | 1.87% | 1400 | 98.13% | 466.6667 | 484.1187 | 2420.5936 |  | Work Hours per Year | 2340
| Number of Eight Foot Hoods | 10 | 1.87% | 1100 | 98.13% | 366.6667 | 380.379 | 3803.79 |  | Non Work Hours per Year | 6420
| Number of Six Foot Hoods | 15 | 1.87% | 800 | 98.13% | 266.6667 | 276.6393 | 4149.589 |  | Annual Sash Open Hours | 163.8
| Number of Five Foot Hoods | 20 | 1.87% | 650 | 98.13% | 216.6667 | 224.7694 | 4495.3881 |  | Annual Sash Closed Hours | 8596.2
| Number of Four Foot Hoods | 25 | 1.87% | 500 | 98.13% | 166.6667 | 172.8995 | 4322.4886
`
|  |  | Observed Average Probability of Active Hood Use | 7% |  |  | Total CFM Exhausted | 19191.8493
Calculations for Constant Volume System at Half Sash Height
|  |  | Per Hood |  |  |  |  | All Hoods
CFM
| Number of Ten Foot Hoods | 5 | 1400 |  |  |  |  | 7000
| Number of Eight Foot Hoods | 10 | 1100 |  |  |  |  | 11000
| Number of Six Foot Hoods | 15 | 800 |  |  |  |  | 12000
| Number of Five Foot Hoods | 20 | 650 |  |  |  |  | 13000
| Number of Four Foot Hoods | 25 | 500 |  |  |  |  | 12500
[7 empty] | Total CFM Exhausted | 55500
Calculations for Constant Volume System at Full Sash Height
|  |  | Per Hood |  |  |  |  | All Hoods
CFM
| Number of Ten Foot Hoods | 5 | 2174.6667 |  |  |  |  | 10873.3333
| Number of Eight Foot Hoods | 10 | 1708.6667 |  |  |  |  | 17086.6667
| Number of Six Foot Hoods | 15 | 1242.6667 |  |  |  |  | 18640
| Number of Five Foot Hoods | 20 | 1009.6667 |  |  |  |  | 20193.3333
| Number of Four Foot Hoods | 25 | 776.6667 |  |  |  |  | 19416.6667
[7 empty] | Total CFM Exhausted | 86210